Tender Specification Bipolar Isolation Amplifier DB 68

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Bipolar Isolation Amplifier, fixed setting

Cost optimized isolation and conversion of bipolar and unipolar standard signals,

slim housing for DIN-rail mounting, installation depth 60 mm, width 11.2 mm, protection class: IP 20

Input			± 20 mA, ± 10 mA, 0 - 20 mA, 4 - 20 mA
			± 10 V, ± 5 V, 0 - 10 V, 2 - 10 V, 0 - 5 V, 1 - 5 V
			see order code
Output			0 - 20 mA, 4 - 20 mA, 0 - 10 mA, 2 - 10 mA
			0 - 10 V, 2 - 10 V, 0 - 5 V, 1 - 5 V
			see order code
Response time		< 2 ms

Transmission error	< 0.2 % full scale

Operation temeprature	–20 °C to +60 °C   (–4 °F to +140 °F)

Power supply		24 V AC/DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Bipolar Isolation Amplifier DB 68 P – __  __  	(see order code)

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

|  |  |  | Input | Output |
| --- | --- | --- | --- | --- |
| DB 68 P – |  |  | X | X |
| Input | 0 - 10 V |  | 0 |  |
|  | 2 - 10 V |  | 6 |  |
|  | ± 10 V |  | 1 |  |
|  | 0 - 5 V |  | 3 |  |
|  | 1 - 5 V |  | 7 |  |
|  | ± 5 V |  | 2 |  |
|  | 0 - 20 mA |  | 8 |  |
|  | 4 - 20 mA |  | 9 |  |
|  | ± 20 mA |  | 4 |  |
|  | ± 10 mA |  | 5 |  |
| Output | 0 - 10 V |  |  | 6 |
|  | 2 - 10 V |  |  | 7 |
|  | 0 - 5 V |  |  | 5 |
|  | 1 - 5 V |  |  | 8 |
|  | 0 - 20 mA |  |  | 2 |
|  | 4 - 20 mA |  |  | 4 |