Tender Specification Repeater Power Supply HART DC 52500

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Repeater Power Supply HART

Powering and Isolation of 2-wire SMART Transmitters with HART communication, 
slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input				0/4 - 20 mA   (4 – 20 mA modulated with HART signal)
				Transmitter supply voltage approx. 16 V, max. 35 mA
				Overload 50 mA

Output				0/4 - 20 mA   (4 – 20 mA modulated with HART signal)

Load 230 - 600 Ohm

Cut-off frequency		100 Hz, > 2.5 kHz HART signal

Transmission error		< 0.1 % full scale

Power supply			16.8 to 31.2 V DC, approx. 1.2 W

Protective separation		EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage			3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage		600 V AC/DC for overvoltage category II and pollution degree 2

Type				Repeater Power Supply HART DC 52500 ___		(see order code)

Supplier			DRAGO Automation GmbH, Berlin, Germany
				Phone: +49-30-409982-0, Fax: +49-30-409982-10, 
				email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

| Repeater Power Supply HART, calibrated range selection | DC 52500 S |
| --- | --- |
| Repeater Power Supply HART, calibrated range selection, In-Rail-Bus for power supply | DC 52500 B |