Tender Specification Passive Transmitter Repeater DC 58

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Passive Transmitter Repeater

Powering and isolation of 2-wire transmitters,

slim housing for DIN-rail mounting, installation depth 60 mm, width 11.2 mm, protection class: IP 20

Input			4 - 20 mA
			Operating current range 2 - 23 mA

Voltage drop approx. 4.7 V (approx. 9.7 V with HART resistor)
			Short circuit input current < 35 mA

Output			4 - 20 mA

Transmission error	< 0.1 % full scale

Operation temeprature	–20 °C to +60 °C   (–4 °F to +140 °F)

Supply voltage		15 to 30 V DC

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Type			Passive Transmitter Repeater DC 58 P

Supplier		DRAGO Automation GmbH, Berlin, Germany

Phone: +49-30-409982-0, Fax: +49-30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent