Tender Specification Isolation Amplifier DN 25000

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Isolation Amplifier, calibrated signal setting

Isolation and conversion of standard signals,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input				0 - 20 mA, 4 - 20 mA
				0 - 10 V, 2 - 10 V 
Output				0 - 20 mA, 4 - 20 mA
				0 - 10 V, 2 - 10 V 
Range setting			calibrated signal setting

Transmission error		< 0.1 % full scale

Cut-off frequency		5 kHz, 100 Hz, 10 Hz, switch selectable

Power supply			9.6 to 31.2 V DC, approx. 0.7 W, In-Rail-Bus

Protective separation		EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage			3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage		600 V AC/DC for overvoltage category II and pollution degree 2

Type				Isolation Amplifier DN 25000 ___	(see order code)

Supplier			DRAGO Automation GmbH, Berlin, Germany

Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10,

email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

| Isolation Amplifier, calibrated range selection | DN 25000 S |
| --- | --- |
| Isolation Amplifier, calibrated range selection, In-Rail-Bus for power supply | DN 25000 B |