Tender Specification Shunt/mV Isolation Amplifier DS 75000

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Shunt/mV Isolation Amplifier, Zero/Span compensation, calibrated signal setting

Isolation and conversion of bipolar and unipolar industrial signals,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input				± 60 mV, ± 100 mV, ± 150 mV, ± 250 mV, ± 300 mV, ± 500 mV
				0 - 60 mV, 0 - 100 mV, 0 - 150 mV, 0 - 250 mV, 0 - 300 mV, 0 - 500 mV

Output				± 20 mA, ± 10 mA, 0 - 20 mA, 4 - 20 mA, 0 - 10 mA, 2 - 10 mA
				± 10 V, ± 5 V, 0 - 10 V, 2 - 10 V, 0 - 5 V, 1 - 5 V
Range setting			calibrated signal setting

Subsequent readjustment	zero/span potentiometers on the front panel, switchable

Cut-off frequency		8 kHz, switchable to 100 Hz

Transmission error		< 0.1 % full scale

Power supply			9.6 to 31.2 V DC, approx. 0.8 W, In-Rail-Bus

Protective separation		EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage			3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage		600 V AC/DC for overvoltage category II and pollution degree 2

Type				Shunt/mV Isolation Amplifier DS 75000 ___		(see order code)

Supplier			DRAGO Automation GmbH, Berlin, Germany
				Phone: +49-(0)30-409982-0, Fax: +49-(0)30-409982-10, 
				email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

| Shunt/mV Isolation Amplifier, calibrated range selection | DS 75000 S |
| --- | --- |
| Shunt/mV Isolation Amplifier, calibrated range selection, In-Rail-Bus for power supply | DS 75000 B |