Tender Specification Pt Temperature Transmitter DT 45200

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

Pt Temperature Transmitter, configurable via DIP switch or USB

for platinium sensors,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input			Pt 100, Pt 200, Pt 500, Pt 1000, Pt 2000	acc. IEC 60751

JPt 50, JPt 100 (TK3916)			acc. JIS C 1604
			Sensor connection: 4-wire, 3-wire, 2-wire
			min. Span: 25 K
Measuring error		< 0.1 K + 0.05 % meas. value

Output (programmable)	0 to  20 mA, 4 to 20 mA, 0 to 5 V, 0 to 10 V 
Transfer characteristic	Rising / falling linearly

Übertragungsfehler	< 0,1 % full scale

Messrate		4 / s

Hilfsenergie		9.6 to 31.2 V DC, approx. 0.8 W, In-Rail-Bus

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Typ			Pt Temperature Transmitter DT 45200 ___		(see order code)

Supplier		DRAGO Automation GmbH, Berlin, Germany
			Tel.: +49-30-409982-0, Fax: +49-30-409982-10, 
			email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

| Pt Temperature transmitter, programmable via USB and DIP switch | DT 45200 S |
| --- | --- |
| Pt Temperature transmitter, programmable via USB and DIP switch, In-Rail-Bus for power supply | DT 45200 B |