Tender Specification KTY Temperature Transmitter DT 45600

Place the cursor in your Web browser's address bar and scan the bar code. You find directly into the right service web portal. 
DRAGO simple – reliable

KTY Temperature Transmitter, configurable via DIP switch or USB

for nickel sensors,

slim housing for DIN-rail mounting, width 6.2 mm, protection class: IP 20

Input			KT100, KT110, KT130, KT210, KT230, KTY10-5, KTY10-6, KTY10-62, KTY10-7, 
			KTY11-5, KTY11-6, KTY11-7, TY13-5, KTY13-6, KTY13-7, KTY16-6, KTY19-6M, 
			KTY19-6Z, KTY21-5, KTY21-6, KTY21-7, KTY23-5, KTY23-6, KTY23-7, KTY81-110, 
			KTY81-120, KTY81-121, KTY81-122, KTY81-210, KTY81-220, KTY81-221, 
			KTY81-222, KTY81-250, KTY81-251, KTY81-252, KTY82-110, KTY82-120, 
			KTY82-121, KTY82-122, KTY82-150, KTY82-151, KTY82-152, KTY82-210, 
			KTY82-220, KTY82-221, KTY82-222, KTY82-250, KTY82-251, KTY82-252, 
			KTY83-110, KTY83-120, KTY83-121, KTY83-122, KTY83-150, KTY83-151, 
			KTY83-152, KTY84-130, KTY84-150, KTY84-151, KTY84-152, ST-13, ST-15, ST-16, 
			ST-20M, ST-20Z
			Sensor connection: 3-wire, 2-wire
			min. Span: 25 K
Measuring error		< 0.3 K + 0.05 % meas. value

Output (programmable)	0 to  20 mA, 4 to 20 mA, 0 to 5 V, 0 to 10 V 
Transfer characteristic	Rising / falling linearly

Übertragungsfehler	< 0.1 % full scale

Messrate		4 / s

Hilfsenergie		9.6 to 31.2 V DC, approx. 0.8 W, In-Rail-Bus

Protective separation	EN 61140, 3-Port isolation up to 300 V AC/DC between all circuits

Test voltage		3 kV, 50 Hz, 1 min., input against output against power supply

Working voltage	600 V AC/DC for overvoltage category II and pollution degree 2

Typ			KTY Temperature Transmitter DT 45600 ___		(see order code)

Supplier		DRAGO Automation GmbH, Berlin, Germany
			Tel.: +49-30-409982-0, Fax: +49-30-409982-10, 
			email: info@drago-automation.de, internet: www.drago-automation.de

or equivalent

Order code:

| KTY Temperature transmitter, programmable via USB and DIP switch | DT 45600 S |
| --- | --- |
| KTY Temperature transmitter, programmable via USB and DIP switch, In-Rail-Bus for power supply | DT 45600 B |